## Slide 1: Central HPWH Work Group
October 20, 2020

## Slide 2
Agenda
What’s New?
Market rate adoptions survey
  https://www.surveymonkey.com/r/ET_CHPWH
Ecosizer1.0 Overview and Demonstration
Central HPWHWG Vision, Roadmap, 2021 workplan
End of year funds

## Slide 3
What’s New
New projects
  Technology and location
New collaboration opportunities
New code, policies or rulemakings
New products

## Slide 4
Market Adoption
https://www.surveymonkey.com/r/ET_CHPWH

## Slide 5
10/20/2020
Ecotope
Colin Grist and Paul Kintner
Ecosizer – Multi-Family CHPWH Sizing Tool
Notes: Fermi paradox  where are they?  one of countless theories suggests advanced civilization wipe themselves out  war… climate change

## Slide 6
Why do we need a sizing tool?
What are we designing to?
Ecosizer Method for sizing.
How to use the Ecosizer.

## Slide 7: Previous Sizing and Equipment Selection
55 Tons
1,000 Gallons
5 Tons
520 Gallons
Notes: Older sizing method leads to at least double what is needed.
Oversizing of single speed equipment will result in unstable operation
Oversizing will not result in cost-effective DHW system
Storage is cheaper than capacity.

## Slide 8: GOALS
Standardize method for all
  Remove the mystery behind getting a size from manufacturers
Standardize schematics
Education  Change is hard

## Slide 9: Domestic Hot Water Load
Chart: Hour of Day
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
Design Day | 0.35714 | 0.14286 | 0.071429 | 0.071429 | 0.071429 | 0.21429 | 1.7857 | 3.5714 | 2.3571 | 1.9286 | 0.5 | 0.57143 | 0.5 | 0.57143 | 0.28571 | 0.14286 | 0.21429 | 0.85714 | 1.2857 | 1.7143 | 2.0714 | 2.1429 | 1.5 | 0.57143
Average Day | 0.36481 | 0.16922 | 0.13259 | 0.084939 | 0.11504 | 0.35252 | 0.98934 | 1.7705 | 1.6611 | 1.2914 | 0.83547 | 0.67121 | 0.5987 | 0.51973 | 0.50035 | 0.512 | 0.5141 | 0.63458 | 0.87452 | 0.98169 | 1.1072 | 1.1445 | 1.007 | 0.6458
Hot water load defined by:
    the number of occupants
    how much hot water they use
At the Design Conditions (cool temperatures)
Notes: First step is predicting the hot water load

## Slide 10: All Heat Pumps Are Not The Same
Single Pass
Heats water to working temp in single pass
Multi-Pass
Heats water to working temp in multiple passes
Notes: Single-Pass vs. muiltipass require completely different design approaches Shawn will speak more on this.
What is important to understand is single pass heats the water in a single pass (typically a 90F lift)
Where multipass heats water in multiple passes. Typically with a 10F lift per pass

## Slide 11
ECOSIZER METHOD
Chart: Hour
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
DHW Demand | 30.3951 | 12.1581 | 6.079 | 6.079 | 6.079 | 18.2371 | 151.9757 | 303.9514 | 200.6079 | 164.1337 | 42.5532 | 48.6322 | 42.5532 | 48.6322 | 24.3161 | 12.1581 | 18.2371 | 72.9483 | 109.4225 | 145.8967 | 176.2918 | 182.3708 | 127.6596 | 48.6322
Hot Water Generation | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Chart: Hour Since Start of Peak
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
0600 Peak | -14.6731 | -157.1322 | -240.156 | -269.688 | -214.8217 | -152.2288 | -68.8336 | 11.5899 | 88.4473 | 165.3046 | 248.6999 | 286.9242 | 317.422 | 290.8618 | 231.6122 | 237.7415 | 255.7578 | 315.3789 | 422.5483 | 538.633 | 660.6612 | 782.6895 | 904.7177 | 1000
1900 Peak | -26.5602 | -85.8098 | -79.6805 | -61.6642 | -2.0431 | 105.1263 | 221.211 | 343.2392 | 465.2675 | 587.2957 | 682.578 | 667.9049 | 525.4458 | 442.422 | 412.89 | 467.7563 | 530.3492 | 613.7444 | 694.1679 | 771.0253 | 847.8826 | 931.2779 | 969.5022 | 1000
Storage Efficiency
T
Aquastat Fraction
Running Volume
Cycling Volume
Idealized Hot Water Storage Tank
Evening Peak
Morning Peak

## Slide 12: TWO DISTINCT LOADS
Primary Heating:
  Heating water for use
  Making cold water hot
Temperature Maintenance:
  Reheating water due to energy losses in the distribution system
  Keeping hot water hot
Chart: 
| Unit Heating | Common Heating | DHW Heating | DHW Temp Maintenance | Unit Plugs and Lights | Common Plugs and Lights
 | 5 | 5 | 6 | 4 | 10 | 10
Notes:   Reheating water due to energy losses in the distribution system
  Temperature maintenance is a significant load year-round. Typically it is 30-50% of the heating load!
  There are a few options to deal with this, the two primary methods are circulating the water or heat tracing the piping
  HW circulation can create issues with heatpump operation if it is not addressed appropriately.
  -Averaged ~30% of the total water heating energy or ~10% of total building energy use*.

## Slide 13: TEMPERATURE MAINTENANCE LOAD
Chart: Recirculation Loop Losses (W/unit)
| Yesler 2E | Grow Building A - Classic Recirc | Grow Building D - Pipe in Pipe
Theoretical | 81.2918 | 74.237 | 43.362
Measured | 86 | 172.0643 | 99.8925
45 measured buildings show variance
Theoretical calculation doesn’t match measured values
Seattle multi-family is typically around 50 – 100 W/apt
Notes: Next is predicting the temperature maintenance load
Median is 90 W/apt
Average is 175 W/apt

## Slide 14
SWING TANK
Chart: Hour Since Start of Peak

## Slide 15
SWING TANK
Swing Tank Volume (Gallons) |  | 
Number of Apartments | Ecosizer | Title 24
0 - 12 | 80 | 80
13 - 24 | 80 | 96
24 - 48 | 80 | 168
49 - 96 | 120 - 300 | 288
> 96 | 120 - 300 | 480
Annual simulation of swing tank suggests the increasing the volume of the tank is not very effective at average temperature maintenance loads (~100 W/apt)
Annually offsetting ~50 W/apt

## Slide 16
PARALLEL TANK
Chart: Time (minutes)
| 0 | 20 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 180
Design | 135 | 125 | 135 | 125 | 135 | 125 | 135 | 125 | 135 | 125
Constant temperature maintenance load
Design to cycle
  On period greater than 20 minutes to prevent short cycling.

## Slide 17
LOAD SHIFTING
Same methodology but hot water generation rate goes to zero
  Checks that it has enough recovery for the whole after the event
Expand storage volume, but still trades off with heating capacity
Comparison
100 people, 2000 gallons per day
HPWH size to run 20 hours
Scenario | Sized Volume (Gallons) | Heating Capacity kBTU/HR
No Load Shift | 530 | 83
5PM to 9PM | 700 | 83
6AM to 10AM and 5PM to 9PM | 950 | 104
Chart: 
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
DHW Demand | 30.3951 | 12.1581 | 6.079 | 6.079 | 6.079 | 18.2371 | 151.9757 | 303.9514 | 200.6079 | 164.1337 | 42.5532 | 48.6322 | 42.5532 | 48.6322 | 24.3161 | 12.1581 | 18.2371 | 72.9483 | 109.4225 | 145.8967 | 176.2918 | 182.3708 | 127.6596 | 48.6322
Hot Water Generation | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Chart: Gallons of DHW per Hour
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
DHW Demand | 30.3951 | 12.1581 | 6.079 | 6.079 | 6.079 | 18.2371 | 151.9757 | 303.9514 | 200.6079 | 164.1337 | 42.5532 | 48.6322 | 42.5532 | 48.6322 | 24.3161 | 12.1581 | 18.2371 | 72.9483 | 109.4225 | 145.8967 | 176.2918 | 182.3708 | 127.6596 | 48.6322
Hot Water Generation Rate | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 100
Chart: Hour Of Day
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
DHW Demand | 30.3951 | 12.1581 | 6.079 | 6.079 | 6.079 | 18.2371 | 151.9757 | 303.9514 | 200.6079 | 164.1337 | 42.5532 | 48.6322 | 42.5532 | 48.6322 | 24.3161 | 12.1581 | 18.2371 | 72.9483 | 109.4225 | 145.8967 | 176.2918 | 182.3708 | 127.6596 | 48.6322
Hot Water Generation Rate | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 0 | 0 | 0 | 0 | 0 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 0 | 0 | 0 | 0 | 0 | 125 | 125 | 125
Notes: For example, in a situation similar to the example worked in Figure EX1 and Figure EX2, if a user sets the load shift period from 1700 to 2000 the assumption is the hot water generation rate goes to 0 during this time period,

## Slide 18: Ecosizer Method

## Slide 19
What users are asking for
  Equipment selection of different available technologies
  Accounting for temperature dependent HPWH performance and defrost by modeling with location-based weather files
Bring in HPWHsim and yearly analysis
  Conduct energy performance and sizing analysis.
  Easily compare multiple scenarios and trade-offs between tank sizes and HPWHs
Chart: Tank Node Temperatures
Chart: Hour Of Day
WHAT’S NEXT? ECOSIM
Notes: This is the tool that is needed to compare PERFORMANCE – different products, different configurations, different options, climates, sizing, controls, etc… Needed by designers to optimize their designs. Needed by code officials and utility program people to determine savings from range of products and designs.
So what’s next? Some of the early feedback suggests users want more, they want to be able to select specific equipment from manufactures and see how much volume they need. And they want us to account for the different defrost deratings from manufactures, as well as encompassing location-based weather files, and they want annual performance.
The good news is that we can solve many of these issues from the continual development of HPWHsim, the premier heat pump water heater modeling software used in CBECC-Res. With this software we can model tank temperatures, input power and COP for specific HPWH technologies and weather files, providing annual performance estimates. And this could allow for users to change the tank sizes or heating capacity to see the trade offs in annual energy usage letting them make informed decisions using cost benefit analysis.

## Slide 20
Paul Kintner paul@ecotope.com
Colin Grist colin@ecotope.com
THANK YOU
INPUT
FUNDERS

## Slide 21
VISION for ROADMAP
High Performance: Low GWP (<700) High Average System Efficiency (C0Psys~3) Grid Responsive
OPPORTUNITIES - END STATE
CODES/INCENTIVES
PROVEN PRODUCTS AVAILABLE
MARKET KNOWS & DESIRES PRODUCT
Sticks. Codes etc require or encourage HPWH Carrots. Utility programs/community-based choice aggregators provide incentives … cost-effective
Collaborative process that encourages and proves proven systems Local suppliers readily have plug-n-play systems available
Market actors know how to design, install and commission systems Market actors are aware and desire the systems
ACTIVITIES / INTERVENTIONS
Advanced Water Heater Spec is available Comment on new codes Develop Model Code Develop Model Incentive Program Credits for modeled systems performance Assist others in development of incentive program EE, Decarb, Grid Interaction Model gas ban Model cost-effective designs for modeled codes
4-5 proven plug-n-play systems Supply chain is trained TIM knowledge development system
Designers/Architects (market actors) are trained and choose to install systems Trades are trained and are comfortable installing systems Operators trained and operations and can optimize the system for performance and load flexibility
Develop a funded 24-month plan/roadmap to develop framework for all new CHPWH systems being non-fossil

## Slide 22
Sample 2021 Work Plan

## Slide 23
ASK:
Does this seem about right?
Join team and contribute expertise or interests
  Continue vision development
  Develop workplan
Next Steps

## Slide 24
End of Year funds
Several project that need funding
  Training
  Spec development
  Market assessment
  Needs assessment
  … other priority items?