## Two Season Loss Factors
TWO SEASON LOSS FACTORS
Summer (Jun-Aug) = | 2.087%
Non-summer (Sept-May) = | 2.039%

## Monthly Loss Factors
MONTHLY LOSS FACTORS | Average Hour (MW) | Loss %
January = | 23487.7711 | 2.161%
February = | 23515.6598 | 2.163%
March = | 21080.7483 | 2.041%
April = | 18828.7583 | 1.927%
May = | 19950.621 | 1.984%
June = | 21568.8574 | 2.065%
July = | 22408.2446 | 2.107%
August = | 22021.1474 | 2.088%
September = | 19431.4898 | 1.958%
October = | 18385.4534 | 1.905%
November = | 21342.3893 | 2.054%
December = | 23509.8248 | 2.162%
|  | 2.051% | Annual Average

## Loss Factor Equations
Spring/Fall Losses |  |  | Average Losses
TTSL | Losses | Loss Factor | TTSL | Losses | :pss Factpr
29714.5651 | 616.3868 | 0.020744 | 34301.9278 | 693.2553 | 0.02021
29913.1574 | 621.9862 | 0.020793 | 34510.3689 | 702.2453 | 0.020349
30123.3875 | 627.7016 | 0.020838 | 34688.0044 | 709.1969 | 0.020445
30335.9305 | 633.5658 | 0.020885 | 34931.4437 | 715.7499 | 0.02049
30544.5261 | 639.423 | 0.020934 | 35139.4509 | 720.2293 | 0.020496
30751.4674 | 645.3872 | 0.020987 | 35348.9715 | 727.2239 | 0.020573
30959.1851 | 651.5835 | 0.021047 | 35565.1498 | 733.0769 | 0.020612
31169.27 | 657.0366 | 0.02108 | 35776.3918 | 739.9062 | 0.020681
31374.7245 | 663.2827 | 0.021141 | 35985.0433 | 749.1259 | 0.020818
31584.5329 | 669.8841 | 0.021209 | 36193.1209 | 754.0082 | 0.020833
31791.0661 | 675.9094 | 0.021261 | 36402.5921 | 761.1945 | 0.02091
| Average | 0.020966 |  | Average | 0.020583
Summer Losses
TTSL | Losses | Loss Factor
38219.91 | 763.0985 | 0.019966
38431.8784 | 776.197 | 0.020197
38538.577 | 782.8952 | 0.020315
38847.2844 | 789.7061 | 0.020328
39047.9603 | 789.7061 | 0.020224
39254.4435 | 796.2338 | 0.020284
39482.5555 | 799.6554 | 0.020253
39689.8219 | 806.4065 | 0.020318
39903.4145 | 820.2919 | 0.020557
40103.9548 | 820.2919 | 0.020454
40309.2808 | 827.4344 | 0.020527
| Average | 0.02029
Winter Losses
TTSL | Losses | Loss Factor
34971.3083 | 700.2806 | 0.020024
35186.071 | 708.5528 | 0.020137
35402.0488 | 716.9938 | 0.020253
35611.1164 | 723.9778 | 0.02033
35825.8662 | 731.5589 | 0.02042
36041.0038 | 740.0508 | 0.020534
36253.7088 | 747.9918 | 0.020632
36470.0835 | 756.2755 | 0.020737
36676.9909 | 763.8032 | 0.020825
36890.875 | 771.8487 | 0.020922
37107.4295 | 780.2397 | 0.021027
| Average | 0.020481

## 3yrs TTSL
Acct | Title | Month | Unit | Hours | Sum | HLH | LLH | Max | Max_Dttm | Min | Min_Dttm
272500 | TOT TRANS SYS LOAD | 2019-01-01 | MWH | 744 | 16924903 | 10000892 | 6924011 | 28498 | 1/2/2019 HE8 | 17238 | 1/24/2019 HE4
272500 | TOT TRANS SYS LOAD | 2019-02-01 | MWH | 672 | 14903409 | 9006924 | 5896485 | 29002 | 2/21/2019 HE8 | 17261 | 2/16/2019 HE3
272500 | TOT TRANS SYS LOAD | 2019-03-01 | MWH | 743 | 15853585 | 9269527 | 6584058 | 27822 | 3/4/2019 HE8 | 16365 | 3/31/2019 HE3
272500 | TOT TRANS SYS LOAD | 2019-04-01 | MWH | 720 | 14511557 | 8768138 | 5743419 | 25392 | 4/9/2019 HE20 | 15517 | 4/20/2019 HE4
272500 | TOT TRANS SYS LOAD | 2019-05-01 | MWH | 744 | 14439953 | 8439000 | 6000953 | 23940 | 5/2/2019 HE8 | 14683 | 5/8/2019 HE4
272500 | TOT TRANS SYS LOAD | 2019-06-01 | MWH | 720 | 14674802 | 8708250 | 5966552 | 27168 | 6/11/2019 HE20 | 14593 | 6/16/2019 HE8
272500 | TOT TRANS SYS LOAD | 2019-07-01 | MWH | 744 | 15638360 | 9506507 | 6131853 | 28563 | 7/26/2019 HE20 | 14192 | 7/22/2019 HE3
272500 | TOT TRANS SYS LOAD | 2019-08-01 | MWH | 744 | 15867145 | 9905653 | 5961492 | 29405 | 8/14/2019 HE19 | 15352 | 8/5/2019 HE4
272500 | TOT TRANS SYS LOAD | 2019-09-01 | MWH | 720 | 14005421 | 7893954 | 6111467 | 28430 | 9/3/2019 HE19 | 14840 | 9/30/2019 HE4
272500 | TOT TRANS SYS LOAD | 2019-10-01 | MWH | 744 | 13289389 | 8162555 | 5126834 | 23660 | 10/29/2019 HE8 | 13140 | 10/13/2019 HE5
272500 | TOT TRANS SYS LOAD | 2019-11-01 | MWH | 721 | 15145904 | 8772231 | 6373673 | 27484 | 11/27/2019 HE18 | 15709 | 11/4/2019 HE2
272500 | TOT TRANS SYS LOAD | 2019-12-01 | MWH | 744 | 16100926 | 9275981 | 6824945 | 27660 | 12/31/2019 HE18 | 16227 | 12/22/2019 HE3
272500 | TOT TRANS SYS LOAD | 2020-01-01 | MWH | 744 | 17395635 | 10273779 | 7121856 | 28666 | 1/14/2020 HE19 | 17963 | 1/5/2020 HE4
272500 | TOT TRANS SYS LOAD | 2020-02-01 | MWH | 696 | 17227357 | 10180514 | 7046843 | 30781 | 2/4/2020 HE19 | 20187 | 2/2/2020 HE15
272500 | TOT TRANS SYS LOAD | 2020-03-01 | MWH | 743 | 15662474 | 9141363 | 6521111 | 29059 | 3/2/2020 HE19 | 16142 | 3/13/2020 HE3
272500 | TOT TRANS SYS LOAD | 2020-04-01 | MWH | 720 | 13543747 | 8127290 | 5416457 | 24929 | 4/29/2020 HE20 | 13595 | 4/13/2020 HE3
272500 | TOT TRANS SYS LOAD | 2020-05-01 | MWH | 744 | 16347003 | 8965653 | 7381350 | 27667 | 5/28/2020 HE21 | 16516 | 5/2/2020 HE8
272500 | TOT TRANS SYS LOAD | 2020-06-01 | MWH | 720 | 16387017 | 9781059 | 6605958 | 28554 | 6/24/2020 HE19 | 18827 | 6/28/2020 HE6
272500 | TOT TRANS SYS LOAD | 2020-07-01 | MWH | 744 | 18290998 | 10675916 | 7615082 | 30093 | 7/16/2020 HE19 | 18336 | 7/26/2020 HE9
272500 | TOT TRANS SYS LOAD | 2020-08-01 | MWH | 744 | 17835753 | 10539271 | 7296482 | 30425 | 8/18/2020 HE19 | 18451 | 8/9/2020 HE9
272500 | TOT TRANS SYS LOAD | 2020-09-01 | MWH | 720 | 14399521 | 8471773 | 5927748 | 27634 | 9/6/2020 HE18 | 14762 | 9/16/2020 HE5
272500 | TOT TRANS SYS LOAD | 2020-10-01 | MWH | 744 | 14504042 | 8909890 | 5594152 | 25278 | 10/1/2020 HE19 | 14833 | 10/20/2020 HE5
272500 | TOT TRANS SYS LOAD | 2020-11-01 | MWH | 721 | 15981194 | 8923116 | 7058078 | 28062 | 11/30/2020 HE19 | 16752 | 11/1/2020 HE4
272500 | TOT TRANS SYS LOAD | 2020-12-01 | MWH | 744 | 17512083 | 10219454 | 7292629 | 28247 | 12/3/2020 HE18 | 18168 | 12/14/2020 HE3
272500 | TOT TRANS SYS LOAD | 2021-01-01 | MWH | 744 | 18104167 | 10254289 | 7849878 | 29313 | 1/26/2021 HE18 | 18299 | 1/1/2021 HE14
272500 | TOT TRANS SYS LOAD | 2021-02-01 | MWH | 672 | 15870851 | 9407492 | 6463359 | 29116 | 2/16/2021 HE19 | 16707 | 2/28/2021 HE16
272500 | TOT TRANS SYS LOAD | 2021-03-01 | MWH | 743 | 15472929 | 9202907 | 6270022 | 28218 | 3/15/2021 HE8 | 14985 | 3/13/2021 HE16
272500 | TOT TRANS SYS LOAD | 2021-04-01 | MWH | 720 | 12614814 | 7607360 | 5007454 | 24092 | 4/7/2021 HE20 | 12358 | 4/17/2021 HE3
272500 | TOT TRANS SYS LOAD | 2021-05-01 | MWH | 744 | 13742830 | 7706473 | 6036357 | 24184 | 5/5/2021 HE20 | 13695 | 5/16/2021 HE8
272500 | TOT TRANS SYS LOAD | 2021-06-01 | MWH | 720 | 15526913 | 9304389 | 6222524 | 28419 | 6/23/2021 HE20 | 13808 | 6/13/2021 HE8
272500 | TOT TRANS SYS LOAD | 2021-07-01 | MWH | 744 | 16085844 | 9450182 | 6635662 | 29379 | 7/2/2021 HE19 | 14587 | 7/29/2021 HE4
272500 | TOT TRANS SYS LOAD | 2021-08-01 | MWH | 744 | 15448303 | 9225879 | 6222424 | 27683 | 8/16/2021 HE19 | 14491 | 8/24/2021 HE3
272500 | TOT TRANS SYS LOAD | 2021-09-01 | MWH | 720 | 13567076 | 8051453 | 5515623 | 24921 | 9/8/2021 HE19 | 13370 | 9/30/2021 HE3
272500 | TOT TRANS SYS LOAD | 2021-10-01 | MWH | 744 | 13242901 | 7862191 | 5380710 | 23599 | 10/5/2021 HE19 | 13066 | 10/17/2021 HE3
272500 | TOT TRANS SYS LOAD | 2021-11-01 | MWH | 721 | 15036490 | 8769386 | 6267104 | 27221 | 11/30/2021 HE18 | 15083 | 11/1/2021 HE2
272500 | TOT TRANS SYS LOAD | 2021-12-01 | MWH | 744 | 18860920 | 10986265 | 7874655 | 31627 | 12/18/2021 HE18 | 18578 | 12/7/2021 HE3

## Base Case vs. Scheduling
Due to difference in how the WECC base cases are measured vs. how the scheduling account measures Total Transmission System Loading, we need to adjust the TTSL from the rotary account 272500, to bring it into the range of the base cases.
The scheduling system doesn't measure "loop-flow," or unscheduled flow through, and so it's always lower. The base cases measure everything in the base case, without regard for schedules.
Winter - December, January, February
Average winter hour from rotary account 272500= | 23504.4186
Average hour from the winter base case = | 36039.682
| 1.5333 | Adjustment Factor
Spring - March, April, May
Average spring hour from rotary account 272500= | 19953.3759
Average hour from the spring base case = | 30751.0739
| 1.5411 | Adjustment Factor
Summer - June, July, August
Average summer hour from rotary account 272500= | 21999.4165
Average hour from the summer base case = | 39257.1892
| 1.7845 | Adjustment Factor
Fall - September, October, November
Average fall hour from rotary account 272500= | 19719.7775
Average hour from the spring base case = | 30751.0739
| 1.5594 | Adjustment Factor
| 1.6046 | Average Adjustment Factor